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                             浙江乐宇电气有限公司

Zhejiang Leyu Electric Co., Ltd   

155W Single Output with Battery Charger (UPS Function)      AD-155 series 
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Features :

Universal AC input / Full range

Protections: Short circuit / Overload / Over voltage

Battery low and battery polarity protection

Cooling by free air convection

100% full load burn-in test

Fixed switching frequency at PFC 67KHz, PWM 134KHz

2 years warranty
SPECIFICATIONS
	MODEL
	AD-155A
	AD-155B
	AD-155C

	OUTPUT

	Output number
	CH1
	CH2
	CH1
	CH2
	CH1
	CH2

	DC voltage
	13.8V
	13.3V
	27.6V
	27.1V
	54V
	53.5V

	Rated Current
	10.5A
	0.5A
	5A 
	0.5A
	2.7A
	0.2A

	Current Range
	0~11.5A
	0-0.5A
	0~5.5A
	0-0.5A
	0-2.7A
	0-0.5A

	Rated Power
	151.55W
	151.55W
	156.5W

	Ripple & Noise
	150mVp-p
	--------
	150mVp-p
	--------
	240mVp-p
	--------

	Voltage Adj. Range
	CH1:12~14.5V
	CH1:24~29V
	CH1:48-58V

	Voltage Tolerance
	±2.0%
	--------
	±1.0%
	--------
	±1.0%
	--------

	Line Regulation
	±0.5%
	--------
	±0.5%
	--------
	±0.5%
	--------

	Load Regulation
	±0.5%
	--------
	±0.5%
	--------
	±0.5%
	--------

	Setup, Rise Time
	1000ms, 90ms/230VAC          2000ms, 90ms/115VAC at full load

	Hold Up Time
	24ms/230VAC          20ms/115VAC at full load

	INPUT

	Voltage Range
	88~264VAC   47~63Hz; 124~370VDC

	AC Current
	2.5A/115VAC          1.5A/230VAC

	Efficiency
	80%
	84%
	84%

	Inrush Current
	Cold start 20A/115VAC   40A/230VAC

	Leakage Current
	<1mA /240VAC

	PROTECTION

	Over Load
	CH1:105 ~ 135%          CH2:0.51 ~ 0.9A rated output power

	
	Protection type: AC Charging Mode: Hiccup mode, recovers automatically after fault condition is removed UPS Mode: Protected by internal fuse

	Over Voltage
	CH1:15.87~18.63V
	CH1:31.74~37.26V
	CH1:62.1 ~ 72.9V

	
	Protection type:Shut down o/p voltage, re-power on to recover

	Battery Low
	10V±0.8V
	19.5V(+1.5V,-1V )
	39V±2V

	ENVIRONMENT

	Working Temp.
	-10~+60℃ (Refer to “Derating Curve”) 

	Working Humidity
	20~90%RH non-condensing

	Storage Temp., Humidity
	-20~+85℃,10~95%RH

	Temp. Coefficient
	±0.03%/ ℃(0~50℃ )

	Vibration
	10~500Hz,2G10min./1cycle,60min.each along X, Y,Z axes 

	SAFETY &EMC

	Safety Standards
	UL60950-1, TUV EN60950-1 

	Withstand Voltage
	I/P-O/P:3KVAC   I/P-FG:1.5KVAC   O/P-FG:0.5KVAC 



	Isolation Resistance
	I/P-O/P,I/P-FG,O/P-FG:100M Ohms/500VDC /25℃ /70%RH 



	EMC Emission
	Compliance to EN55022(CISPR22) Class B, EN61000-3-2,-3 

	EMC Immunity
	Compliance to EN61000-4-2,3,4,5,6,8,11,EN55024,light industry level, criteria A 

	OTHERS

	Dimension
	199*110*50mm (L*W*H)

	Weight
	0.88Kg

	Packing
	16pcs/carton/15kg/0.95CUFT

	NOTE

	1. All parameters NOT specially mentioned are measured at 230VAC input, rated load and 25℃ of ambient temperature.

2. Ripple & noise are measured at 20MHz of bandwidth by using a 12” twisted pair-wire terminated with a 0.1uf & 47uf parallel capacitor.
3. Tolerance: includes set up tolerance, line regulation and load regulation.
4. The power supply is considered a component which will be installed into a final equipment. The final equipment must be re-confirmed that it still meets EMC directives.
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