60W Single Output Industrial DIN Rail Power Supply         HDR-60 series

| Model | HDR-60-5 | HDR-60-12 | HDR-60-15 | HDR-60-24 | HDR-60-48 |
| --- | --- | --- | --- | --- | --- |
| DC Voltage | 5V | 12V | 15V | 24V | 48V |
| Rated Current | 6.5A | 4.5A | 4A | 2.5A | 1.25A |
| Current Range | 0 ~ 6.5A | 0 ~ 4.5A | 0 ~ 4A | 0 ~ 2.5A | 0 ~ 1.25A |
| Rated Power | 32.5W | 54W | 60W | 60W | 60W |
| Ripple & Noise (max.) | 80mVp-p | 120mVp-p | 120mVp-p | 150mVp-p | 240mVp-p |
| Voltage Adj. Range | 5.0 ~ 5.5V | 10.8 ~ 13.8V | 13.5 ~ 18V | 21.6 ~ 29V | 43.2 ~ 55.2V |
| Voltage Tolerance | ±2.0% | ±1.0% | ±1.0% | ±1.0% | ±1.0% |
| Line Regulation | ±1.0% | ±1.0% | ±1.0% | ±1.0% | ±1.0% |
| Load Regulation | ±1.0% | ±1.0% | ±1.0% | ±1.0% | ±1.0% |
| Setup, Rise Time | 500ms, 50ms/230VAC 500ms, 50ms/115VAC at full load |  |  |  |  |
| Hold Up Time | 30ms/230VAC 12ms/115VAC at full load |  |  |  |  |
| Voltage Range | 85 ~ 264VAC (277VAC operational ) 120 ~ 370VDC (390VDC operational ) |  |  |  |  |
| Frequency Range | 47 ~ 63Hz |  |  |  |  |
| Efficiency | 85% | 88% | 89% | 90% | 91% |
| AC Current | 1.2A/115VAC 0.8A/230VAC |  |  |  |  |
| Inrush Current | COLD START 30A/115VAC 60A/230VAC |  |  |  |  |
| Over Load | 105 ~ 160% rated output power |  |  |  |  |
|  | Hiccup mode when output voltage <50%, recovers automatically after fault condition is removed |  |  |  |  |
|  | Constant current limiting within 50% ～100% rated output voltage, recovers automatically after fault condition is removed |  |  |  |  |
| Over Voltage | 5.75 ~ 6.75V | 14.2 ~ 16.2V | 18.8 ~ 22.5V | 30 ~ 36V | 56.5 ~ 64.8V |
|  | Protection type : Shut down o/p voltage, re-power on to recover |  |  |  |  |
| Working Temp. | -30 ~ +70℃ (Refer to "Derating Curve") |  |  |  |  |
| Working Humidity | 20 ~ 90% RH non-condensing |  |  |  |  |
| Storage Temp., Humidity | -40 ~ +85℃, 10 ~ 95% RH non-condensing |  |  |  |  |
| Temp. Coefficient | ±0.03%/℃ (0 ~ 50℃) RH non-condensing |  |  |  |  |
| Vibration | 10 ~ 500Hz, 2G 10min./1cycle, period for 60min. each along X, Y, Z axes; Mounting: Compliance to IEC60068-2-6 |  |  |  |  |
| Operating Altitude | 2000 meters |  |  |  |  |
| Withstand Voltage | I/P-O/P:4KVAC |  |  |  |  |
| Isolation Resistance | I/P-O/P:100M Ohms / 500VDC / 25℃/ 70% RH |  |  |  |  |
| MTBF | 927.6K hrs min. MIL-HDBK-217F (25℃) |  |  |  |  |
| Dimension | 53*90*54.5mm (L*W*H) |  |  |  |  |
| Packing | 190g;60pcs/12.4Kg/0.97CUFT |  |  |  |  |
| 1. All parameters NOT specially mentioned are measured at 230VAC input, rated load and 25℃ of ambient temperature. |  |  |  |  |  |
| 2. Ripple & noise are measured at 20MHz of bandwidth by using a 12” twisted pair-wire terminated with a 0.1μf & 47μf parallel capacitor. |  |  |  |  |  |
| 3. Tolerance : includes set up tolerance, line regulation and load regulation. |  |  |  |  |  |
| 4. The power supply is considered as an independent unit, but the final equipment still need to re-confirm that the whole system complies with the EMC directives. For guidance on how to perform these EMC tests, please refer to “EMI testing of component power supplies.” |  |  |  |  |  |
| 5. The ambient temperature derating of 3.5℃/1000m with fanless models and of 5℃/1000m with fan models for operating altitude higher than 2000m(6500ft). |  |  |  |  |  |