
480W Single Output Industrial DIN Rail Power Supply        NDR-480 series
	SPECIFICATIONS

	OUTPUT
	

	Model
	NDR-480-24
	NDR-480-48

	DC Voltage 
	24V
	48V

	Rated Current 
	20A
	10A

	Current Range 
	0-20A
	0-10A

	Rated Power 
	480W
	480W

	Ripple & Noise 
	240mVp-p
	480mVp-p

	Voltage Adj. Range 
	21-28V
	43-53V

	Voltage Tolerance 
	±1%
	±1%

	Setup, Rise Time 
	1200ms,40ms/230VAC   800ms,40ms/115VAC at full load

	Hold Up Time 
	24ms/230VAC   24ms/115VAC at full load

	
	

	INPUT
	

	Voltage Range 
	176~264VAC   47~63Hz; 240~370VDC

	AC Current
	2.8A/115V   1.4A/230V

	Efficiency
	84%
	85%

	Inrush Current 
	Cold start 27A/115V   45A/230V

	Leakage Current
	<3.5mA/240VAC

	
	

	PROTECTION
	

	Over Load 
	105%~150% 

	
	Protection type: Constant current limiting, recovers automatically after fault condition is removed

	Over Voltage 
	30-36V
	54-60V

	
	Protection type: Shut down o/p voltage, re-power on to recover

	Over Temp.
	100℃±5℃(TSW1)

	
	Protection type: Shut down o/p voltage, recovers automatically after temperature goes down

	
	

	ENVIRONMENT
	

	Working Temp., Humidity
	-10℃~+70℃; 20%~90%RH

	Storage Temp., Humidity
	-20℃~+85℃; 10%~95%RH

	Vibration
	10~500Hz, 2G 10min./1cycle, period for 60min, each along X, Y, Z axes

	
	

	SAFETY
	

	Withstand Voltage
	I/P-O/P: 3KVAC   I/P-FG: 1.5KVAC   O/P-FG: 0.5KVAC

	Isolation Resistance
	I/P-O/P, I/P-FG, O/P-FG: 100M Ohms / 500VDC

	
	

	STANDARD
	

	Safety Standard
	Design refer to UL508,UL60950-1, TUV EN60950-1

	EMC Standard
	EN55011,EN55022,EN61000-3-2,-3,EN61000-4-2,3,4,5,6,8,11,ENV50204,EN55024,EN61000-6-2(EN50082-2)

	
	

	OTHERS
	

	Dimension
	125.5*125.2*100mm(L*W*H)

	Weight
	1.3Kg

	Packing
	12pcs/15.5Kg/1.2CUFT

	
	

	NOTE
	

	1. All parameters NOT specially mentioned are measured at 230VAC input, rated load and 25℃ of ambient temperature. 

2. Ripple & noise are measured at 20MHz of bandwidth by using a 12” twisted pair-wire terminated with a 0.1μ & 47μ parallel capacitor. 

3 .Tolerance: includes set up tolerance, line regulation and load regulation.

4. The power supply is considered a component which will be installed into a final equipment. The final equipment must be re-confirmed that it still meets EMC directives.

5 . Derating may be needed under low input voltages. Please check the derating curve for more details.


Features: 
Universal AC input/ full range 
Built-in active PFC function 
Protections: Short circuit/ Over load/ Over voltage/ Over temperature 
Cooling by free air convection 
Can be installed on DIN rail TS-35/7.5 or 15 
LED indicator for power on 
100% full load burn-in test 
Fixed switching frequency at 100KHz 
2 year warranty 

[image: image1.jpg]MMechanical Specification

D o oo

ADMISSTBLE DIN-RAIL

MDerating Curve

100
S
® 0
e '
* 5
° 4
. & .
I I
ssina Terninal Pin No. Assignnent (TB1)

10 e
T\
~

) R

B o)

2 o

3

)

w0 W2 W @ wse

WBIENT BTG (©

OB

in No. | Aesigment
T ¥
2 oy
3 AL

Terminal Pin No. Assignaent (TB2)

Bin No. | Rssignment]
1.2 [0 ot
3.4 {oc oureur-T]

MOutput Derating VS Input Voltage

st
|
10 5 [T

INPOT YOLTAGE() 608





