| Model |  | SC-120-12 |  | SC-120-24 |  |
| --- | --- | --- | --- | --- | --- |
| Output | DC voltage | CH1:13.8V | CH1:13.4V | CH1:27.6V | CH2:26.5V |
|  | Voltage tolerance | ±1% | ----- | ±1% | ----- |
|  | Rated current | 8A | 0.5A | 4A | 0.3A |
|  | Current range | 0~8A | ----- | 0~4A | ----- |
|  | Rated power | 117.1W |  | 118.4W |  |
|  | Ripple&noise | 120mvp-p | ----- | 180mvp-p | ----- |
|  | DC voltage ADJ.range | CH1:11.3~14.9V |  | CH1:21.3~29.8V |  |
| Input | Voltage range | 90~264VAC/127~370VDC |  |  |  |
|  | frequency | 47~63HZ |  |  |  |
|  | AC current | 2.8A/115VAC,1.4A/230VAC |  |  |  |
|  | efficiency | 81% |  | 83% |  |
|  | Inrush current | Cold start current 30A/115VAC,50A/230VAC |  |  |  |
|  | Leakage current | < 1mA/240VAC |  |  |  |
| Protection | Over load | Rated output power110%~150% start over load protection |  |  |  |
|  |  | protection mode: AC charging mode:hiccup mode auto-recovery after fault condition is removed |  |  |  |
|  | Battery protection At low voltage | 9.5~11V |  | 20~22V |  |
|  |  | Protection mode:cut off output |  |  |  |
| Function | UPS introduction | long-term online floating charge to battery,high charging efficiency,battery can saturate to more than 90% ,cauto-stop harging when it's full,prevent over charging. Effectively extend battery life,AC/battery auto switch,no switch time,no need human guard,cold-start ,when there is no AC input ,can use battery start UPS,Meet the user's emergency needs |  |  |  |
| Environment | Working temp,humidity | -10°C~+60°C,20%~90%RH |  |  |  |
|  | Storage temp,humidity | -20°C~+85°C,10%~95%RH non-condensing |  |  |  |
|  | Withstand vibration | 10~500HZ,2G 10min/1cycle,period for 60 minutes,each axes |  |  |  |
| Safety | Withstand voltage | I/P-O/P:3KVAC I/P-FG:1.5KVAC O/P-FG:0.5KVAC |  |  |  |
|  | Isolated resistance | I/P-O/P,I/P-FG,O/P-FG:100Mohms/500VDC |  |  |  |
| Fit standard | Safety standard | Compliance to UL60950-1 |  |  |  |
|  | EMC standard | Compliance to EN55022,CLASSB |  |  |  |
| others | Dimension | 159*97*38mm(L*W*H) |  |  |  |
|  | Weight/packing | 0.56kg/45pcs/26kg/0.041m⊃3;/1.45CUFT |  |  |  |
| note | 1. All parameters NOT specially mentioned are measured at 230VAC input, rated load and25°Cof ambient temperature. 2. Ripple & noise are measured at 20MHz of bandwidth by using a 12" twisted pair-wire terminated with a 0.1uf & 47uf parallel capacitor. 3. Tolerance : includes set up tolerance, line regulation and load regulation. |  |  |  |  |