
ZSN3-5K0 智能工业电源



	Model
	ZSN3-5K0-12
	ZSN3-5K0-24
	ZSN3-5K0-36
	ZSN3-5K0-48
	ZSN3-5K0-72
	ZSN3-5K0-96
	ZSN3-5K0-110
	ZSN3-5K0-150
	ZSN3-5K0-220

	




OUTPUT
	DC Voltage
	12V
	24V
	36V
	48V
	72V
	96V
	110V
	150V
	220V

	
	Rated Current
	333A
	208A
	138.8A
	104A
	69A
	52A
	45A
	33A
	22.7A

	
	Current Range
	0 - 333A
	0 - 208A
	0 - 138.8A
	0 - 104A
	0 - 69A
	0 - 52A
	0 - 45A
	0 - 33A
	0 - 22.7A

	
	Rated Power
	4000W
	5000W

	
	Ripple
	250mV
	270mV
	300mV
	400mV
	500mV
	600mV
	850mV
	900mV
	1000mV

	
	Optimal Range of Constant Current
	6 - 12V
	12 - 24V
	18 - 36V
	24 - 48V
	36 - 72V
	48 - 96V
	55 - 110V
	75 - 150V
	110 - 220V

	
	voltage accuracy
	± 1.0%

	
	linear adjustment rate
	± 1.0%

	
	load regulation
	± 1.0%

	
	Setup, Rise, Hold Up Time
	1500mS，100mS/230VAC(at full load）

	INPUT
	Voltage Range
	180 - 264VAC / 245 - 370VDC

	
	Frequency Range
	45Hz - 65Hz

	
	 power factor
	PF≧0.6/230VAC(at full load)

	
	Efficiency
	83 %
	86 %
	87 %
	89 %
	90 %
	90 %
	90 %
	91 %
	91 %

	
	AC Current
	＜ 55A

	
	Leakage Current
	＜ 3.0mA / 240VAC

	PROTECTION
	short circuit
	Enter a constant current

	
	Over Temp
	The output is turned off, and it automatically resumes or restarts when the temperature drops




	FUNCTION
	output voltage adjustment
	0 - 13.2V
	0 - 26.4V
	0 - 39.6V
	0 - 52.8V
	0 - 79.2V
	0 - 105.6V
	0 - 121V
	0 - 165V
	0 - 242V

	
	constant current output adjustment
	0 - 333A
	0 - 208A
	0 - 138.8A
	0 - 104A
	0 - 69A
	0 - 52A
	0 - 45A
	0 - 33A
	0 - 22.7A

	
	External potentiometer
	External potentiometer control (voltage, current)

	
	Analog voltage control
	0 - 5V / 0 - 10V Control (voltage, current)

	
	Auxiliary power supply
	12V 0.5A

	
	remote control switch
	By default, it will be powered on and powered off at a high level （3V-12V）

	ENVIRONMENT
	Working Temp
	-20 - +60℃

	
	Working Humidity
	-20 - 90% RH No condensation

	
	Storage Temp., Humidity
	-40 - +85℃, 10 - 95% RH No condensation

	
	vibration resistance
	10 - 500Hz, 2G 10 min/cycle, 60 minutes each in X, Y, and Z axes

	SAFETY
	Insulation resistance
	Input-to-output:100Mhms/500VDC/25℃/70%RH

	
	Withstand Voltage
	I/P-O/P :1.2KVAC  I/P-FG:1.2KVAC  O/P-FG:0.5KVAC

	
	
	

	
	
	

	OTHERS
	Dimension
	356*216*80mm（L*W*H）

	
	Weight
	6.5 KG
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	1. All parameters are measured at 230VAC input, rated load and 25°C unless otherwise specified.
2. RIPPLE AND NOISE VOLTAGES ARE MEASURED AT 20UMHz bandwidth oscilloscope with 0.1 μ and 47 μ capacitance at the end of a 12-inch twisted pair cable, measured at 20MHZ bandwidth.
3. Accuracy: including setting error, linear regulation and load regulation.
4. If the input voltage is low, the output needs to be derated, please refer to the static characteristic curve for details.
5. The start-up time is measured when the machine is cool-in, and frequent switching on and off may increase the start-up time.













